{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["样板"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"样板","index":0,"n_rows":18,"n_cols":9,"rows_kept":18,"merged":[[0,0,0,8]],"flags":["formulas_cached_only"]}
["   新中轴（中区）南大巴及环形车道集水井水泵维修工程量清单"]
["序号","名称","品牌","型号规格","位置","故障/处理方法","单位","数量","备注"]
[1,"潜水泵","格兰富","集水井电箱编号：1-D2QSAP2, 3.7KW潜水泵","楼层-2东车道（P13)","排水缓慢、振动大/维修更换叶轮、清理底坑及拆装人工","台",1]
[2,"潜水泵","格兰富","集水井电箱编号：1-D2QSAP35, 3.7KW潜水泵","楼层-2东西道（P13)","排水缓慢、噪音大/更换轴承、控制箱不自动、清理底坑及拆装人工","台",1,"控制箱维修"]
[3,"潜水泵","格兰富","集水井电箱编号：新增（图编2-002）, 3.7KW潜水泵","楼层-东西道（P13)53#雨水泵房旁","泵体故障/维修线圈，更换机械密封、轴承、清理底坑及拆装人工","台",1]
[4,"潜水泵","格兰富","  集水井电箱编号：2-D2QSAP21, 3.7KW潜水泵","楼层-2东西道（拐进P3)","反水、排水缓慢/维修线圈，更换叶轮、控制箱不自动、清理底坑及拆装人工","台",1,"控制箱维修"]
[5,"潜水泵","格兰富","集水井电箱编号：1-D1QSAP30,1.5KW潜水泵","南大巴车场东集水井","水泵故障/维修线圈，更换机械密封、轴承、控制箱不自动、清理底坑及拆装人工","台",1,"控制箱维修"]
[6,"潜水泵","格兰富","集水井电箱编号：1-D1QSAP20, 1.5KW潜水泵","南大巴车场东集水井","水泵故障、跳闸/维修线圈，更换机械密封、轴承、电缆、清理底坑及拆装人工","台",1]
[7,"潜水泵","格兰富","集水井电箱编号：1-D1QSAP22, 1.5KW潜水泵","南大巴车场东集水井","排水缓慢/维修水泵、清理底坑及拆装人工","台",1]
[8,"潜水泵","格兰富","集水井电箱编号：1-D1QSAP23, 1.5KW潜水泵","南大巴车场东集水井","排水缓慢、噪音大/更换叶轮、控制箱不自动、清理底坑及拆装人工","台",1,"控制箱维修"]
[9,"潜水泵","格兰富","集水井电箱编号：1-D1QSAP24, 1.5KW潜水泵","南大巴车场东集水井","排水缓慢/维修水泵、清理底坑及拆装人工","台",1]
[10,"潜水泵","格兰富","集水井电箱编号：1-D1QSAP9, 1.5KW潜水泵","负一楼海印卸货区","排水缓慢/维修水泵、清理底坑及拆装人工","台",1]
[11,"潜水泵","格兰富","集水井电箱编号：1-D1QSAP13, 1.5KW潜水泵","南大巴车场西集水井","排水缓慢、跳闸/维修线圈，更换机械密封、轴承、电缆、清理底坑及拆装人工","台",1]
[12,"潜水泵","格兰富","集水井电箱编号：1-D1QSAP12, 1.5KW潜水泵","南大巴车场西集水井","排水缓慢/维修水泵、清理底坑及拆装人工","台",1]
[13,"潜水泵","格兰富","集水井电箱编号：1-D1QSAP11, 1.5KW潜水泵","南大巴车场西集水井","排水缓慢/维修水泵、清理底坑及拆装人工","台",1]
[14,"潜水泵","格兰富","集水井电箱编号：1-D1QSAP5, 1.5KW潜水泵","南大巴车场西集水井","水泵故障、跳闸/维修线圈，更换机械密封、轴承、电缆、清理底坑及拆装人工","台",1]
[15,"潜水泵","格兰富","集水井电箱编号：1-D1QSAP8, 1.5KW潜水泵","南大巴车场西集水井","排水缓慢/维修水泵、清理底坑及拆装人工","台",1]
[16,"潜水泵","格兰富","集水井电箱编号：1-D1QSAP6, 1.5KW潜水泵","南大巴车场西集水井","水泵故障、跳闸/维修线圈，更换机械密封、轴承、电缆、控制箱不自动、清理底坑及拆装人工","台",1,"控制箱维修"]