{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["工程量清单"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"工程量清单","index":0,"n_rows":23,"n_cols":9,"rows_kept":23,"merged":[[0,0,0,8],[20,0,20,6]],"flags":["formulas_cached_only"]}
[" 花城汇（中区、北区）水泵维修项目工程量清单"]
["序号","位置","型号规格","故障/处理方法","单位","数量","单价","合计","备注"]
[1,"楼层-2 P8车库","3.7kw潜水泵","排水缓慢/检测维修及拆装人工","台",1,null,null,"集水井电箱编号：1-D2QSAP69"]
[2,"楼层-2 P8车库","3.7kw潜水泵","排水缓慢、噪音大/更换轴承及拆装人工","台",1,null,null,"集水井电箱编号：2-D2QSAP5"]
[3,"楼层-2 P11车库","3.7kw潜水泵","排水缓慢、/更换叶轮、轴承及拆装人工","台",1,null,null,"集水井电箱编号：1-D2QSAP37"]
[4,"楼层-2 P11车库","3.7kw潜水泵","排水缓慢/更换叶轮、检修及拆装人工","台",1,null,null,"集水井电箱编号：1-D2QSAP34（图编2-007）"]
[5,"楼层-2 歌剧院站东北扶梯（P9）","3.7kw潜水泵","排水缓慢/检测维修及拆装人工","台",2,null,null,"集水井电箱编号：1-D2SAP17"]
[6,"喷泉西面","3.7kw潜水泵，风井内高度1.9米","水泵故障跳闸/重绕线圈，更换密封套件、轴承 及拆装人工","台",1,null,null,"风井集水井电箱编号：1-D1SAP5dm"]
[7,"图书馆对面风机房内","3.7kw潜水泵","控制箱跳热继电维修/更换水泵线圈、轴承、密封套件及拆装人工","台",1,null,null,"集水井电箱编号：1-D1QSAP32"]
[8,"海印第三下沉口广场东面","3.7kw潜水泵，风井内高度1.8米","水泵故障跳闸/重绕线圈，更换密封套件、轴承及拆装人工","台",1,null,null,"风井集水井电箱编号：2-D1SAP2dm之一"]
[9,"中区负二层西车道","Q=3L/s H=24m N=4.8KW(图纸参数）","污水泵故障/重绕线圈，更换密封套件、轴承及拆装人工","台",1,null,null,"25#雨污水泵房"]
[10,"中区负二层西车道","N=7.5KW","污水泵故障/重绕线圈，更换密封套件、轴承及拆装人工","台",1,null,null,"42#雨污水泵房"]
[11,"中区负二层东车道","H:22M,Q:4L/S N:3KW(图纸参数）","污水泵故障/重绕线圈，更换密封套件、轴承及拆装人工","台",1,null,null,"45#雨污水泵房"]
[12,"P2车库东边车道","格兰富 H:21M,P:3.5KW,Q:3L/H,(图纸参数）","污水泵故障/重绕线圈，更换密封套件、轴承及拆装人工","台",1,null,null,"62#雨污水泵房"]
[13,"P1车场","格兰富8.7KW/污水泵","1、水泵轴承（SKF）； 633.00 2、水泵电机定子线圈；1050.00 3、水泵机械密封（格兰富）； 3352.00 4、加注水泵冷却润滑白腊油脂； 350.00 5、水泵各处密封O型圈（格兰富）； 300.00 6、现场安装、调试； 760.00","台",1,null,null,"109#污水泵房          2-D2AP13-18"]
[14,"6#污水泵房（116#污水房）","格兰富8.7KW/污水泵","1、水泵轴承（SKF）； 633.00 2、水泵电机定子线圈；1050.00 3、水泵机械密封（格兰富）； 3352.00 4、加注水泵冷却润滑白腊油脂； 350.00 5、水泵各处密封O型圈（格兰富）； 300.00 6、现场安装、调试； 760.00","台",1,null,null,"116#污水泵房          2-D2AP3-17"]
[15,"西通道","格兰富7.5KW/雨水泵","1、水泵轴承（SKF）； 633.00 2、水泵电机定子线圈；905.00 3、水泵机械密封（格兰富）； 3352.00 4、加注水泵冷却润滑白腊油脂； 350.00 5、水泵各处密封O型圈（格兰富）； 300.00 6、现场安装、调试； 760.00","台",1,null,null,"113强电房（集水井）   2-D1SAP1-1"]
[16,"北区1号隔油池","格兰富7.5KW/雨水泵","1、水泵轴承（SKF）； 633.00 2、水泵电机定子线圈；905.00 3、水泵机械密封（格兰富）； 3352.00 4、加注水泵冷却润滑白腊油脂； 350.00 5、水泵各处密封O型圈（格兰富）； 300.00 6、现场安装、调试； 760.00","台","1",null,null,"隔油池房（集水井）    1-D2GYAP1"]
[17,"9#污水泵房（124#污水房）","格兰富8.7KW/污水泵","1、水泵轴承（SKF）； 633.00 2、水泵电机定子线圈；1050.00 3、水泵机械密封（格兰富）； 3352.00 4、加注水泵冷却润滑白腊油脂； 350.00 5、水泵各处密封O型圈（格兰富）； 300.00 6、现场安装、调试； 760.00","台","1",null,null,"污水泵房（124#污水房）2-D2AP8-25"]
[18,"110#污水泵房","格兰富8.7KW/污水泵","1、水泵轴承（SKF）； 633.00 2、水泵电机定子线圈；1050.00 3、水泵机械密封（格兰富）； 3352.00 4、加注水泵冷却润滑白腊油脂； 350.00 5、水泵各处密封O型圈（格兰富）； 300.00 6、现场安装、调试； 760.00","台",1,null,null,"110#污水泵房"]
["总计"]
[{"$nulls":3},"报价单位：（盖章）"]
[{"$nulls":3},"联系人及联系电话："]